## Sheet1
Fire and Life Safety
| Requirement | Completed By: | Temporary Alternative | Current Status | Achieved Use
1 | Install Fire Alarm System throughout (work ready number) | 2018-08-01 |  | Completed 10/24/18 | Limited use of the gym and recreation offices. Occupant load 300 max. Prohibited use as a dance hall, discotheque, night club, or festival seating.
2 | Install Emergency Lights in basement | 2018-08-01
Replace all emergency light batteries throughout
| Install Emergency Light outside recreation office |  |  | Completed 8/18
3 | Remove the stage curtains, replace stage curtains $4500, or treat stage curtains | 2018-08-01
4 | Remove wooden closet to the right of the stage | 2018-08-01 |  | Completed 5/18
5 | Fire proof paint remainder exposed wood (material only) | 2018-08-01 |  | Completed 7/18
6 | Remove wood from mezzanine | 2018-08-01 |  | Completed 5/18
7 | Remove stairs to the mezzanine | 2018-08-01 |  | Completed 2018
8 | Ground water service to the building steel | 2018-08-01 |  | Completed 8/18
Bond both ends of steel conduit encasing electrode conductors
Consolidate circuits eliminating tandem breakers
Provide fill plates in breaker boxes
Replace non-working GFCI outlets
Replace vending machine outlet with GFCI
Provide missing box and device covers
(note: this price includes disconnecting generator and is a work ready number)
9 | Remove the wooden closets behind the stage | 2018-08-01 |  | Completed 7/18
10 | Provide an exit discharge. Exterior sidewalk from door to curb. (material only) | 2018-08-01 |  | Completed 6/18
11 | Replace doors between gym and storage area behind stage with 1-1/2 rating (estimate based on Bob Cummings, awaiting estimate from Philbrook G/C) | 2019-08-01 | Discontinue use of this space | Completed 10/24/18 | Low hazard storage for area behind stage.
12 | Complete the fire separation between the stage and storage area behind (estimate based on Bob Cummings, awaiting estimate from Philbrook G/C) | 2019-08-01 | Discontinue use of this space | Completed 10/24/18
13 | Exit threshold in storage area behind stage (estimate from Philbrook G/C) | 2019-08-01 | Discontinue use of this space | Completed 10/24/18
14 | Develop operational plan/layout for community group storage behind the stage | 2019-08-01 | Discontinue use of this space | Completed
15 | Remove griddle, clean hood, remove existing extinguishing system, conduct health inspection of kitchen. Modify the function permit process to include an in-depth review of cooking per event. | 2019-08-01 | Review/permit cooking activities. Restrict preparation of foods that create grease laden vapors. | Completed 2019 | Limited kitchen use until 8/1/23 (see line 20)
16 | Provide fire protection clearances for generator | 2019-08-01 | Remove or disable | Gen Removed | Emergency back up power to facility.
17 | Provide generator fuel tank protection | 2025-08-01 | Remove or disable | Gen Removed
18 | Install 1 hour fire separation in basement (rough estimate based on Bob Cummings) | 2025-08-01 | Install fire alarm system |  | Compliance
19 | Replace hood and suppression system | 2025-08-01 | Modify or prohibit kitchen use |  | Full commercial kitchen use
20 | Install proper fire separation between kitchen and gym | 2025-08-01 | Modify or prohibit kitchen use
21 | Install voice annunciation to fire alarm system, other coverages, and fire extinguisher monitoring. | 2025-08-01 | Install minimal detection and alarm |  | Compliance and occupant load to 430
22 | Provide proper fire separation from old fd and rec offices | 2025-08-01 | Install fire alarm and discontinue old fd use. |  | Low hazard storage in old FD bay areas.
23 | Provide proper fire separation from old fd and gym | 2025-08-01 | Install fire alarm and discontinue old fd use
24 | Install exit in fire bay to meet remoteness requirement | 2025-08-01 | Discontinue use or remove
25 | Install Fire Suppression System throughout | 2028-08-01 | Prohibit activities that would trigger this requirement: vehicle storage, high hazard storage, dances, festival seating, night club, discotheque. |  | Full assembly use and less stringent exiting requirements from second floor.
26 | Provide proper exiting from old fd second floor and re evaluate emergency lighting. | 2028-08-01 | Discontinue use or remove |  | Use of old fd business space and 2nd floor meeting room
27 | Provide for AFCI Protection in old bunk room | 2028-08-01 | Discontinued use or remove
28 | Provide additional receptacles in high use work spaces (old fd) | 2028-08-01 | Discontinued use or remove
29 | Provide for clearance of panel in old bunk room | 2028-08-01 | Keep area clear |  | Compliance
30 | Replace all outlets in Vehicle Bays to GFCI | 2028-08-01 | Discontinued use or remove |  | Compliance
31 | Provide proper fire separation fire separation from rec offices and gym | 2028-08-01 | Install fire alarm and monitor storage |  | Compliance